## Heat Loads
Spefific Heat [Btu/lb F]
0.24
Density [lb/ft3]
0.0749
60 | min/hr
1.0786 | Factor to convert HDD to BTU/CFM
City | HDD65 | BTU/CFM heat load for continuous operation
Fort Madison | 5270 | 136416.2688
Lincoln | 5882 | 152258.1581
Cape Girardeau | 4507 | 116665.6781
Kaiser | 4629 | 119823.7018
Knob Noster | 4818 | 124716.0499
Kansas City | 5444 | 140920.3354
St Louis | 4843 | 125363.1859

## PGE Workpaper Data
Food Service Facility Type | Institutional | Casual Dining | Hotel | Super | University Campus | Average
| Cafeteria1 | Restaurant2 | Main Kitchen3 | Market4 | Dining Facility5
Location | San Ramon | Rancho | San Francisco | Brentwood | Berkeley
Cucamonga
Exhaust Capacity (cfm) | 9600 | 6400 | 22500 | 23800 | 12000 | 14860
Rated Exhaust | 6 | 3 | 15 | NA | 7 | 7.75
Fan Power (HP)
Measured Exhaust | 4.2 | 2.3 | 7.6 | 6.3 | 6.22 | 5.32
Fan Power (kW)
Exhaust kW/HP Ratio | 0.7 | 0.77 | 0.51 | NA | 0.89 | 0.72
Rated MUA | NA | 5 | 20 | NA | NA | 12.5
Fan Power (HP)
Measured MUA | 3.1 | 1.5 | 6.4 | NA | 6.52 | 4.38
Fan Power (kW)
Measured Total | 7.3 | 3.9 | 14 | 6.29 | 12.47 | 8.79
Fan Power (kW)
Avg Power with DVC (kW) | 1.9 | 2.1 | 5.3 | 1.23 | 5.6 | 3.23
Fan Power Reduction (kW) | 5.4 | 1.8 | 8.7 | 5.1 | 6.8 | 5.56
Fan Power Reduction (%) | 74 | 46 | 62 | 80 | 55 | 64
Fan Speed Reduction (%) | 36 | 19 | 28 | 42 | 23 | 30
Effective CFM | 3471 | 1200 | 6223 | 9986 | 2791 | 4734
Reduction (cfm)
Operating Time (h) | 19 | 17 | 24 | 12 | 17 | 17.8
Baseline Energy Use | 137.9 | 58.9 | 336 | 75.5 | 216.6 | 165
(w/o DVC, kWh/d)
Measure Energy Use | 34.8 | 31.6 | 127 | 17.5 | 97.9 | 61.8
(w/ DVC, kWh/d)
Energy Savings (kWh/d) | 103.1 | 27.3 | 209 | 58 | 118.7 | 103.2
Energy savings (%) | 75 | 46 | 62 | 77 | 55 | 63
Operating Days Per Year | 260 | 363 | 365 | 360 | 300 | 330
Annual Energy Savings (kWh) | 26806 | 9910 | 76285 | 20880 | 35610 | 33898
Applied Rate ($/kWh) | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13
Annual Cost Savings ($) | 3485 | 1288 | 9917 | 2714 | 4629 | 4407
Incremental Measure Cost ($) | 12000 | 8000 | 15000 | 18000 | 16000 | 13800
Estimated Useful Life (EUL) a | 15 years | 15 years | 15 years | 15 years | 15 years | 15 years
Estimated Payback (yr) | 3.4 | 6.2 | 1.5 | 6.6 | 3.5 | 3.1
Normalized Baseline Annual Energy Consumption (kWh/exh HP) | [5 empty] | 7640 | 1.3006 | Baseline Hourly Consumption
Normalized Measure Case Annual Energy Consumption (kWh/exh HP) | [5 empty] | 3154 | 0.53694 | Efficient Hourly Consumption
Normalized Annual Energy Savings (kWh/exh HP) | [5 empty] | 4486 | 0.7637 | Hourly Savings
Normalized Demand Savings (kW/exh HP) | [5 empty] | 0.76
Normalized Measure Cost ($/exh HP)b | [5 empty] | 1988
Normalized Annual Energy Cost Savings ($/exh HP) | [5 empty] | 583
CFM reduction per exh HP | 578.5 | 400 | 414.8667 |  | 398.7143 | 448.0202