## Original Illinois Factors
COP assumed for heat pump: | 3
Heating | [5 empty] | Cooling + Fan
GAS HEATING
Building Type | Therm_Savings_Factor (Therm/1000 SqFt) |  |  |  |  | Building Type | Cooling_Savings_Factor (kWh/1000 SqFt) |  |  |  |  | Approx. SqFt per Space |  | Occupancy Schedule |  | Building Type | [7 empty] | Occupancy Schedule |  | Building Type
| Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) |  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) | Building Type | Square Footage | Weekday |  | Elementary School | High School | College/ University | Healthcare Clinic | lodging | Manufacturing | Special Assembly Auditorium | Default | Weekday |  | Office - Low-rise | Office - Mid-rise | Office - High-rise | Religious Building | Restaurant | Retail - Department Store | Retail - Strip Mall | Convenience Store
Office - Low-rise | 30 | 26 | 23 | 22 | 19 | Office - Low-rise | 454 | 456 | 460 | 456 | 462 | Office - Low-rise | 7500
Office - Mid-rise | 19.9184 | 17 | 15 | 15 | 13 | Office - Mid-rise | 430 | 431 | 432 | 428 | 433 | Office - Mid-rise | 50000 | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 75% | 100% | 100% | 96.43% | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Office - High-rise | 26.7577 | 23.4316 | 21 | 19.5292 | 17 | Office - High-rise | 448 | 450 | 452 | 449 | 454 | Office - High-rise | 537600 | 5:00 | 7:00 | 10% | 10% | 10% | 50% | 75% | 50% | 10% | 30.71% | 5:00 | 7:00 | 10% | 10% | 10% | 30% | 80% | 10% | 10% | 30%
Religious Building | 191.3101 | 169.1395 | 150 | 142.8086 | 128 | Religious Building | 493 | 509 | 573 | 584 | 605 | Religious Building | 30000 | 7:00 | 10:00 | 100% | 100% | 100% | 70% | 75% | 100% | 30% | 82.14% | 7:00 | 10:00 | 100% | 100% | 100% | 50% | 50% | 30% | 30% | 75%
Restaurant | 135.4115 | 122.0629 | 106 | 103.5822 | 91 | Restaurant | 505 | 515 | 553 | 569 | 581 | Restaurant | 7500 | 10:00 | 13:00 | 50% | 50% | 60% | 70% | 50% | 20% | 100% | 57.14% | 10:00 | 13:00 | 60% | 60% | 60% | 50% | 100% | 70% | 70% | 90%
Retail - Department Store | 46.6697 | 41.7375 | 37 | 36.1585 | 32 | Retail - Department Store | 620 | 625 | 630 | 638 | 642 | Retail - Department Store | 45000 | 13:00 | 15:00 | 100% | 100% | 100% | 70% | 50% | 100% | 100% | 88.57% | 13:00 | 15:00 | 100% | 100% | 100% | 50% | 30% | 70% | 70% | 30%
Retail - Strip Mall | 31.2031 | 27.3404 | 25 | 23.6349 | 21 | Retail - Strip Mall | 380 | 376 | 356 | 406 | 407 | Retail - Strip Mall | 3000 | 15:00 | 18:00 | 20% | 20% | 50% | 50% | 50% | 50% | 50% | 41.43% | 15:00 | 18:00 | 50% | 50% | 50% | 50% | 100% | 100% | 50% | 75%
Convenience Store | 22.8825 | 20.6303 | 18 | 17.4874 | 15 | Convenience Store | 602 | 603 | 610 | 612 | 614 | Convenience Store | 6000 | 18:00 | 24:00 | 100% | 100% | 50% | 100% | 75% | 50% | 100% | 82.14% | 18:00 | 24:00 | 50% | 50% | 50% | 100% | 50% | 50% | 100% | 50%
Elementary School | 83.4091 | 72.5556 | 64 | 60.0759 | 53 | Elementary School | 317 | 327 | 352 | 352 | 363 | Elementary School | 75000 | Weekend | [9 empty] | Weekend
High School | 81.397 | 70.7757 | 63 | 58.5062 | 52 | High School | 305 | 316 | 340 | 340 | 352 | High School | 225000 | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
College/University | 160.7785 | 141.324 | 124 | 119.8521 | 101 | College/University | 392 | 410 | 434 | 449 | 462 | College/University | 1000000 | 5:00 | 7:00 | 100% | 100% | 100% | 50% | 75% | 100% | 10% | 76.43% | 5:00 | 7:00 | 100% | 100% | 100% | 30% | 80% | 10% | 10% | 30%
Healthcare Clinic | 56.7348 | 50.2644 | 44 | 42.3205 | 38 | Healthcare Clinic | 353 | 358 | 379 | 383 | 389 | Healthcare Clinic | 67500 | 7:00 | 10:00 | 100% | 100% | 100% | 70% | 75% | 100% | 30% | 82.14% | 7:00 | 10:00 | 100% | 100% | 100% | 100% | 50% | 30% | 30% | 75%
lodging | 26.0763 | 23.2889 | 20 | 19.5279 | 20 | lodging | 576 | 578 | 586 | 588 | 591 | lodging | 56000 | 10:00 | 13:00 | 100% | 100% | 100% | 70% | 50% | 100% | 100% | 88.57% | 10:00 | 13:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 90%
Manufacturing | 21.2696 | 18.6033 | 16 | 15.3307 | 14 | Manufacturing | 481 | 482 | 482 | 477 | 482 | Manufacturing | 250000 | 13:00 | 15:00 | 100% | 100% | 100% | 70% | 50% | 100% | 100% | 88.57% | 13:00 | 15:00 | 100% | 100% | 100% | 50% | 30% | 100% | 100% | 30%
Special Assembly Auditorium | 225.0365 | 198.4255 | 179 | 174.8265 | 153.7761 | Special Assembly Auditorium | 410 | 427 | 479 | 494 | 513.8065 | Special Assembly Auditorium | 35000 | 15:00 | 18:00 | 100% | 100% | 100% | 50% | 50% | 100% | 80% | 82.86% | 15:00 | 18:00 | 100% | 100% | 100% | 50% | 100% | 100% | 100% | 75%
Default | 77.257 | 68.172 | 60.3333 | 58.0427 | 51.1851 | Default | 451.0667 | 457.5333 | 474.5333 | 481.6667 | 490.0538 | Default | 159673.3333 | 18:00 | 24:00 | 100% | 100% | 100% | 100% | 75% | 100% | 100% | 96.43% | 18:00 | 24:00 | 100% | 100% | 100% | 100% | 50% | 50% | 100% | 50%
(HEAT PUMP with COP = 3 )
Building Type | Heating-HP_Savings_Factor (kWh/1000 SqFt)
| Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion)
Office - Low-rise | 234.4666 | 203.2044 | 179.7577 | 171.9422 | 148.4955
Office - Mid-rise | 155.6734 | 132.8644 | 117.2333 | 117.2333 | 101.6022
Office - High-rise | 209.1263 | 183.1307 | 164.1266 | 152.6312 | 132.8644
Religious Building | 1495.1941 | 1321.9189 | 1172.3329 | 1116.1283 | 1000.3908
Restaurant | 1058.3159 | 953.989 | 828.4486 | 809.5519 | 711.2153
Retail - Department Store | 364.7495 | 326.2019 | 289.1755 | 282.5988 | 250.0977
Retail - Strip Mall | 243.8693 | 213.6807 | 195.3888 | 184.7195 | 164.1266
Convenience Store | 178.8397 | 161.237 | 140.68 | 136.6734 | 117.2333
Elementary School | 651.8884 | 567.0624 | 500.1954 | 469.5264 | 414.2243
High School | 636.1625 | 553.151 | 492.3798 | 457.258 | 406.4088
College/University | 1256.5729 | 1104.5255 | 969.1286 | 936.7107 | 789.3708
Healthcare Clinic | 443.4137 | 392.8443 | 343.8843 | 330.7578 | 296.991
lodging | 203.801 | 182.0156 | 156.3111 | 152.6211 | 156.3111
Manufacturing | 166.2336 | 145.3952 | 125.0488 | 119.8178 | 109.4177
Special Assembly Auditorium | 1758.7844 | 1550.8051 | 1398.984 | 1366.3658 | 1201.8451
Default | 603.8061 | 532.8017 | 471.5384 | 453.6358 | 400.0396
ELECTRIC RESISTANCE
Building Type | Heating-ER_Savings_Factor (kWh/1000 SqFt)
| Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion)
Office - Low-rise | 703.3998 | 609.6131 | 539.2732 | 515.8265 | 445.4865
Office - Mid-rise | 467.0202 | 398.5932 | 351.6999 | 351.6999 | 304.8066
Office - High-rise | 627.379 | 549.3921 | 492.3798 | 457.8935 | 398.5932
Religious Building | 4485.5823 | 3965.7566 | 3516.9988 | 3348.385 | 3001.1723
Restaurant | 3174.9477 | 2861.967 | 2485.3458 | 2428.6558 | 2133.646
Retail - Department Store | 1094.2484 | 978.6057 | 867.5264 | 847.7965 | 750.2931
Retail - Strip Mall | 731.608 | 641.0421 | 586.1665 | 554.1584 | 492.3798
Convenience Store | 536.519 | 483.7111 | 422.0399 | 410.0203 | 351.6999
Elementary School | 1955.6653 | 1701.1871 | 1500.5862 | 1408.5793 | 1242.6729
High School | 1908.4876 | 1659.4529 | 1477.1395 | 1371.774 | 1219.2263
College/University | 3769.7186 | 3313.5765 | 2907.3857 | 2810.1322 | 2368.1125
Healthcare Clinic | 1330.241 | 1178.5329 | 1031.653 | 992.2734 | 890.973
lodging | 611.4029 | 546.0469 | 468.9332 | 457.8634 | 468.9332
Manufacturing | 498.7008 | 436.1857 | 375.1465 | 359.4535 | 328.2532
Special Assembly Auditorium | 5276.3533 | 4652.4152 | 4196.9519 | 4099.0973 | 3605.5353
Default | 1811.4183 | 1598.4052 | 1414.6151 | 1360.9073 | 1200.1189
Heating savings -
For gas,
For heat pump,
For electric resistance,
Where, and
Heating savings -
For gas, 〖 𝑄〗_ℎ𝑒𝑎𝑡𝑖𝑛𝑔= (1.08∗ ∆𝑇∗𝐶𝐹𝑀)/(𝜂_𝑏𝑜𝑖𝑙𝑒𝑟∗100,000 𝐵𝑇𝑈/𝑡ℎ𝑒𝑟𝑚)
For heat pump, 𝑄_ℎ𝑒𝑎𝑡𝑖𝑛𝑔= (1.08∗ ∆𝑇∗𝐶𝐹𝑀)/(𝜂_𝐻𝑃∗3,412 𝐵𝑇𝑈/𝑘𝑊)
For electric resistance, 𝑄_ℎ𝑒𝑎𝑡𝑖𝑛𝑔= (1.08∗ ∆𝑇∗𝐶𝐹𝑀)/(3,412 𝐵𝑇𝑈/𝑘𝑊)
Where, 𝜂_𝑏𝑜𝑖𝑙𝑒𝑟=0.8 and 𝜂_𝐻𝑃=3

## Average Factors per CHD,HDH
COP assumed for heat pump: | 3
Heating | [6 empty] | Cooling + Fan
GAS HEATING
Building Type | Therm_Savings_Factor (Therm/1000 SqFt) / HDH65 | [5 empty] | Building Type | Cooling_Savings_Factor (kWh/1000 SqFt) | [5 empty] | Approx. SqFt per Space |  | Occupancy Schedule |  | Building Type | [7 empty] | Occupancy Schedule |  | Building Type
| Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) | AVERAGE |  | Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion) | AVERAGE | Building Type | Square Footage | Weekday |  | Elementary School | High School | College/ University | Healthcare Clinic | lodging | Manufacturing | Special Assembly Auditorium | Default | Weekday |  | Office - Low-rise | Office - Mid-rise | Office - High-rise | Religious Building | Restaurant | Retail - Department Store | Retail - Strip Mall | Convenience Store
Office - Low-rise | 0.00017058 | 0.00016675 | 0.00016971 | 0.00016702 | 0.00016675 | 0.00016816 | Office - Low-rise | 0.019299 | 0.018738 | 0.014407 | 0.013219 | 0.013475 | 0.015828 | Office - Low-rise | 7500
Office - Mid-rise | 0.00011326 | 0.00010903 | 0.00011068 | 0.00011388 | 0.00011409 | 0.00011219 | Office - Mid-rise | 0.018279 | 0.017711 | 0.01353 | 0.012407 | 0.012629 | 0.014911 | Office - Mid-rise | 50000 | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 75% | 100% | 100% | 96.43% | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Office - High-rise | 0.00015214 | 0.00015027 | 0.00015495 | 0.00014826 | 0.0001492 | 0.00015097 | Office - High-rise | 0.019044 | 0.018491 | 0.014157 | 0.013016 | 0.013242 | 0.01559 | Office - High-rise | 537600 | 5:00 | 7:00 | 10% | 10% | 10% | 50% | 75% | 50% | 10% | 30.71% | 5:00 | 7:00 | 10% | 10% | 10% | 30% | 80% | 10% | 10% | 30%
Religious Building | 0.0010878 | 0.0010847 | 0.0011068 | 0.0010842 | 0.0011234 | 0.0010974 | Religious Building | 0.020957 | 0.020916 | 0.017946 | 0.01693 | 0.017646 | 0.018879 | Religious Building | 30000 | 7:00 | 10:00 | 100% | 100% | 100% | 70% | 75% | 100% | 30% | 82.14% | 7:00 | 10:00 | 100% | 100% | 100% | 50% | 50% | 30% | 30% | 75%
Restaurant | 0.00076995 | 0.00078283 | 0.00078213 | 0.00078638 | 0.00079865 | 0.00078399 | Restaurant | 0.021467 | 0.021162 | 0.01732 | 0.016495 | 0.016946 | 0.018678 | Restaurant | 7500 | 10:00 | 13:00 | 50% | 50% | 60% | 70% | 50% | 20% | 100% | 57.14% | 10:00 | 13:00 | 60% | 60% | 60% | 50% | 100% | 70% | 70% | 90%
Retail - Department Store | 0.00026536 | 0.00026768 | 0.00027301 | 0.00027451 | 0.00028084 | 0.00027228 | Retail - Department Store | 0.026356 | 0.025682 | 0.019731 | 0.018495 | 0.018725 | 0.021798 | Retail - Department Store | 45000 | 13:00 | 15:00 | 100% | 100% | 100% | 70% | 50% | 100% | 100% | 88.57% | 13:00 | 15:00 | 100% | 100% | 100% | 50% | 30% | 70% | 70% | 30%
Retail - Strip Mall | 0.00017742 | 0.00017534 | 0.00018447 | 0.00017943 | 0.0001843 | 0.00018019 | Retail - Strip Mall | 0.016154 | 0.015451 | 0.01115 | 0.01177 | 0.011871 | 0.013279 | Retail - Strip Mall | 3000 | 15:00 | 18:00 | 20% | 20% | 50% | 50% | 50% | 50% | 50% | 41.43% | 15:00 | 18:00 | 50% | 50% | 50% | 50% | 100% | 100% | 50% | 75%
Convenience Store | 0.00013011 | 0.00013231 | 0.00013282 | 0.00013276 | 0.00013165 | 0.00013193 | Convenience Store | 0.025591 | 0.024778 | 0.019105 | 0.017741 | 0.017909 | 0.021025 | Convenience Store | 6000 | 18:00 | 24:00 | 100% | 100% | 50% | 100% | 75% | 50% | 100% | 82.14% | 18:00 | 24:00 | 50% | 50% | 50% | 100% | 50% | 50% | 100% | 50%
Elementary School | 0.00047427 | 0.00046532 | 0.00047223 | 0.00045609 | 0.00046515 | 0.00046661 | Elementary School | 0.013476 | 0.013437 | 0.011025 | 0.010204 | 0.010588 | 0.011746 | Elementary School | 75000 | Weekend | [9 empty] | Weekend
High School | 0.00046282 | 0.00045391 | 0.00046485 | 0.00044417 | 0.00045637 | 0.00045643 | High School | 0.012965 | 0.012985 | 0.010649 | 0.0098563 | 0.010267 | 0.011344 | High School | 225000 | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
College/University | 0.00091419 | 0.00090636 | 0.00091495 | 0.0009099 | 0.00088641 | 0.00090636 | College/University | 0.016664 | 0.016848 | 0.013593 | 0.013016 | 0.013475 | 0.014719 | College/University | 1000000 | 5:00 | 7:00 | 100% | 100% | 100% | 50% | 75% | 100% | 10% | 76.43% | 5:00 | 7:00 | 100% | 100% | 100% | 30% | 80% | 10% | 10% | 30%
Healthcare Clinic | 0.00032259 | 0.00032236 | 0.00032466 | 0.00032129 | 0.0003335 | 0.00032488 | Healthcare Clinic | 0.015006 | 0.014711 | 0.01187 | 0.011103 | 0.011346 | 0.012807 | Healthcare Clinic | 67500 | 7:00 | 10:00 | 100% | 100% | 100% | 70% | 75% | 100% | 30% | 82.14% | 7:00 | 10:00 | 100% | 100% | 100% | 100% | 50% | 30% | 30% | 75%
lodging | 0.00014827 | 0.00014936 | 0.00014757 | 0.00014825 | 0.00017553 | 0.0001538 | lodging | 0.024485 | 0.023751 | 0.018353 | 0.017046 | 0.017238 | 0.020175 | lodging | 56000 | 10:00 | 13:00 | 100% | 100% | 100% | 70% | 50% | 100% | 100% | 88.57% | 10:00 | 13:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 90%
Manufacturing | 0.00012094 | 0.00011931 | 0.00011806 | 0.00011639 | 0.00012287 | 0.00011951 | Manufacturing | 0.020447 | 0.019806 | 0.015096 | 0.013828 | 0.014058 | 0.016647 | Manufacturing | 250000 | 13:00 | 15:00 | 100% | 100% | 100% | 70% | 50% | 100% | 100% | 88.57% | 13:00 | 15:00 | 100% | 100% | 100% | 50% | 30% | 100% | 100% | 30%
Special Assembly Auditorium | 0.0012796 | 0.0012726 | 0.0013208 | 0.0013273 | 0.0013496 | 0.00131 | Special Assembly Auditorium | 0.017429 | 0.017546 | 0.015002 | 0.014321 | 0.014986 | 0.015857 | Special Assembly Auditorium | 35000 | 15:00 | 18:00 | 100% | 100% | 100% | 50% | 50% | 100% | 80% | 82.86% | 15:00 | 18:00 | 100% | 100% | 100% | 50% | 100% | 100% | 100% | 75%
Default | 0.00043928 | 0.00043721 | 0.00044518 | 0.00044065 | 0.00044922 |  | Default | 0.019175 | 0.018801 | 0.014862 | 0.013963 | 0.014293 |  | Default | 159673.3333 | 18:00 | 24:00 | 100% | 100% | 100% | 100% | 75% | 100% | 100% | 96.43% | 18:00 | 24:00 | 100% | 100% | 100% | 100% | 50% | 50% | 100% | 50%
(HEAT PUMP with COP = 3 )
Building Type | Heating-HP_Savings_Factor (kWh/1000 SqFt)
| Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion)
Office - Low-rise | 0.0013332 | 0.0013032 | 0.0013264 | 0.0013054 | 0.0013033
Office - Mid-rise | 0.00088516 | 0.0008521 | 0.00086502 | 0.00089002 | 0.0008917
Office - High-rise | 0.0011891 | 0.0011745 | 0.001211 | 0.0011588 | 0.0011661
Religious Building | 0.0085017 | 0.0084779 | 0.0086502 | 0.0084735 | 0.0087798
Restaurant | 0.0060176 | 0.0061183 | 0.0061128 | 0.006146 | 0.0062419
Retail - Department Store | 0.002074 | 0.002092 | 0.0021337 | 0.0021455 | 0.002195
Retail - Strip Mall | 0.0013866 | 0.0013704 | 0.0014417 | 0.0014024 | 0.0014404
Convenience Store | 0.0010169 | 0.0010341 | 0.001038 | 0.0010376 | 0.0010289
Elementary School | 0.0037066 | 0.0036368 | 0.0036908 | 0.0035646 | 0.0036354
High School | 0.0036172 | 0.0035475 | 0.0036331 | 0.0034714 | 0.0035668
College/University | 0.0071449 | 0.0070837 | 0.0071508 | 0.0071114 | 0.0069278
Healthcare Clinic | 0.0025213 | 0.0025194 | 0.0025374 | 0.0025111 | 0.0026065
lodging | 0.0011588 | 0.0011673 | 0.0011534 | 0.0011587 | 0.0013718
Manufacturing | 0.00094521 | 0.00093247 | 0.00092269 | 0.00090964 | 0.00096029
Special Assembly Auditorium | 0.01 | 0.0099458 | 0.010323 | 0.010373 | 0.010548
Default | 0.0034332 | 0.003417 | 0.0034793 | 0.0034439 | 0.0035109
ELECTRIC RESISTANCE
Building Type | Heating-ER_Savings_Factor (kWh/1000 SqFt)
| Zone 1 (Rockford) | Zone 2 (Chicago) | Zone 3 (Springfield) | Zone 4 (Belleville) | Zone 5 (Marion)
Office - Low-rise | 0.0039995 | 0.0039097 | 0.0039791 | 0.0039161 | 0.0039098
Office - Mid-rise | 0.0026555 | 0.0025563 | 0.0025951 | 0.0026701 | 0.0026751
Office - High-rise | 0.0035673 | 0.0035234 | 0.0036331 | 0.0034763 | 0.0034982
Religious Building | 0.025505 | 0.025434 | 0.025951 | 0.025421 | 0.026339
Restaurant | 0.018053 | 0.018355 | 0.018338 | 0.018438 | 0.018726
Retail - Department Store | 0.0062219 | 0.0062761 | 0.0064011 | 0.0064364 | 0.0065849
Retail - Strip Mall | 0.0041599 | 0.0041112 | 0.0043251 | 0.0042071 | 0.0043213
Convenience Store | 0.0030507 | 0.0031022 | 0.0031141 | 0.0031128 | 0.0030867
Elementary School | 0.01112 | 0.01091 | 0.011072 | 0.010694 | 0.010906
High School | 0.010852 | 0.010643 | 0.010899 | 0.010414 | 0.0107
College/University | 0.021435 | 0.021251 | 0.021452 | 0.021334 | 0.020783
Healthcare Clinic | 0.0075638 | 0.0075583 | 0.0076122 | 0.0075332 | 0.0078195
lodging | 0.0034764 | 0.003502 | 0.0034601 | 0.003476 | 0.0041155
Manufacturing | 0.0028356 | 0.0027974 | 0.0027681 | 0.0027289 | 0.0028809
Special Assembly Auditorium | 0.030001 | 0.029838 | 0.030968 | 0.03112 | 0.031644
Default | 0.0103 | 0.010251 | 0.010438 | 0.010332 | 0.010533
Heating savings -
For gas,
For heat pump,
For electric resistance,
Where, and
Heating savings -
For gas, 〖 𝑄〗_ℎ𝑒𝑎𝑡𝑖𝑛𝑔= (1.08∗ ∆𝑇∗𝐶𝐹𝑀)/(𝜂_𝑏𝑜𝑖𝑙𝑒𝑟∗100,000 𝐵𝑇𝑈/𝑡ℎ𝑒𝑟𝑚)
For heat pump, 𝑄_ℎ𝑒𝑎𝑡𝑖𝑛𝑔= (1.08∗ ∆𝑇∗𝐶𝐹𝑀)/(𝜂_𝐻𝑃∗3,412 𝐵𝑇𝑈/𝑘𝑊)
For electric resistance, 𝑄_ℎ𝑒𝑎𝑡𝑖𝑛𝑔= (1.08∗ ∆𝑇∗𝐶𝐹𝑀)/(3,412 𝐵𝑇𝑈/𝑘𝑊)
Where, 𝜂_𝑏𝑜𝑖𝑙𝑒𝑟=0.8 and 𝜂_𝐻𝑃=3

## Missouri Factors
COP assumed for heat pump: | 3
Heating | [7 empty] | Cooling + Fan
GAS HEATING
Building Type | Therm_Savings_Factor (Therm/1000 SqFt) | [6 empty] | Building Type | Cooling_Savings_Factor (kWh/1000 SqFt) | [6 empty] | Approx. SqFt per Space |  | Occupancy Schedule |  | Building Type | [7 empty] | Occupancy Schedule |  | Building Type
| North East (Fort Madison, IA) | North West (Lincoln, NE) | South East (Cape Girardeau, MO) | South West (Kaiser, MO) | St Louis, MO | Kansas City, MO | Average/Unknown (Knob Noster, MO) |  | North East (Fort Madison, IA) | North West (Lincoln, NE) | South East (Cape Girardeau, MO) | South West (Kaiser, MO) | St Louis, MO | Kansas City, MO | Average/Unknown (Knob Noster, MO) | Building Type | Square Footage | Weekday |  | Elementary School | High School | College/ University | Healthcare Clinic | lodging | Manufacturing | Special Assembly Auditorium | Default | Weekday |  | Office - Low-rise | Office - Mid-rise | Office - High-rise | Religious Building | Restaurant | Retail - Department Store | Retail - Strip Mall | Convenience Store
Office - Low-rise | 21.9228 | 24.4723 | 18.5263 | 19.2658 | 19.9522 | 22.5234 | 20.3097 | Office - Low-rise | 475.013 | 532.7534 | 535.3565 | 633.5317 | 648.5487 | 554.9546 | 578.8244 | Office - Low-rise | 7500
Office - Mid-rise | 14.6255 | 16.3264 | 12.3596 | 12.8529 | 13.3109 | 15.0262 | 13.5493 | Office - Mid-rise | 447.5103 | 501.9077 | 504.36 | 596.851 | 610.9986 | 522.8235 | 545.3112 | Office - Mid-rise | 50000 | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 75% | 100% | 100% | 96.43% | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
Office - High-rise | 19.6811 | 21.9699 | 16.6319 | 17.2958 | 17.912 | 20.2203 | 18.2329 | Office - High-rise | 467.8797 | 524.753 | 527.317 | 624.0179 | 638.8094 | 546.6209 | 570.1322 | Office - High-rise | 537600 | 5:00 | 7:00 | 10% | 10% | 10% | 50% | 75% | 50% | 10% | 30.71% | 5:00 | 7:00 | 10% | 10% | 10% | 30% | 80% | 10% | 10% | 30%
Religious Building | 143.0627 | 159.6999 | 120.8978 | 125.7235 | 130.2031 | 146.9822 | 132.5356 | Religious Building | 566.5862 | 635.4579 | 638.5627 | 755.6642 | 773.5763 | 661.9391 | 690.4105 | Religious Building | 30000 | 7:00 | 10:00 | 100% | 100% | 100% | 70% | 75% | 100% | 30% | 82.14% | 7:00 | 10:00 | 100% | 100% | 100% | 50% | 50% | 30% | 30% | 75%
Restaurant | 102.2069 | 114.0929 | 86.3718 | 89.8194 | 93.0197 | 105.007 | 94.6861 | Restaurant | 560.5565 | 628.6952 | 631.767 | 747.6223 | 765.3437 | 654.8946 | 683.063 | Restaurant | 7500 | 10:00 | 13:00 | 50% | 50% | 60% | 70% | 50% | 20% | 100% | 57.14% | 10:00 | 13:00 | 60% | 60% | 60% | 50% | 100% | 70% | 70% | 90%
Retail - Department Store | 35.4966 | 39.6247 | 29.9971 | 31.1945 | 32.3059 | 36.4691 | 32.8847 | Retail - Department Store | 654.1909 | 733.7114 | 737.2963 | 872.5039 | 893.1854 | 764.2871 | 797.1607 | Retail - Department Store | 45000 | 13:00 | 15:00 | 100% | 100% | 100% | 70% | 50% | 100% | 100% | 88.57% | 13:00 | 15:00 | 100% | 100% | 100% | 50% | 30% | 70% | 70% | 30%
Retail - Strip Mall | 23.4914 | 26.2233 | 19.8518 | 20.6442 | 21.3798 | 24.135 | 21.7628 | Retail - Strip Mall | 398.52 | 446.9623 | 449.1461 | 531.5119 | 544.1107 | 465.5884 | 485.6143 | Retail - Strip Mall | 3000 | 15:00 | 18:00 | 20% | 20% | 50% | 50% | 50% | 50% | 50% | 41.43% | 15:00 | 18:00 | 50% | 50% | 50% | 50% | 100% | 100% | 50% | 75%
Convenience Store | 17.1992 | 19.1993 | 14.5345 | 15.1147 | 15.6532 | 17.6704 | 15.9336 | Convenience Store | 630.9861 | 707.686 | 711.1437 | 841.5553 | 861.5033 | 737.1771 | 768.8846 | Convenience Store | 6000 | 18:00 | 24:00 | 100% | 100% | 50% | 100% | 75% | 50% | 100% | 82.14% | 18:00 | 24:00 | 50% | 50% | 50% | 100% | 50% | 50% | 100% | 50%
Elementary School | 60.831 | 67.9053 | 51.4064 | 53.4583 | 55.3631 | 62.4976 | 56.3549 | Elementary School | 352.5085 | 395.3578 | 397.2896 | 470.1457 | 481.2899 | 411.8334 | 429.5473 | Elementary School | 75000 | Weekend | [9 empty] | Weekend
High School | 59.5031 | 66.4229 | 50.2842 | 52.2914 | 54.1545 | 61.1333 | 55.1247 | High School | 340.4639 | 381.8491 | 383.7148 | 454.0816 | 464.845 | 397.7618 | 414.8704 | High School | 225000 | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 1:00 | 5:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
College/University | 118.1603 | 131.9016 | 99.8536 | 103.8393 | 107.5391 | 121.3976 | 109.4657 | College/University | 441.7419 | 495.4381 | 497.8588 | 589.1576 | 603.1228 | 516.0843 | 538.2822 | College/University | 1000000 | 5:00 | 7:00 | 100% | 100% | 100% | 50% | 75% | 100% | 10% | 76.43% | 5:00 | 7:00 | 100% | 100% | 100% | 30% | 80% | 10% | 10% | 30%
Healthcare Clinic | 42.3541 | 47.2796 | 35.7921 | 37.2208 | 38.547 | 43.5145 | 39.2375 | Healthcare Clinic | 384.3617 | 431.083 | 433.1892 | 512.6287 | 524.7799 | 449.0473 | 468.3618 | Healthcare Clinic | 67500 | 7:00 | 10:00 | 100% | 100% | 100% | 70% | 75% | 100% | 30% | 82.14% | 7:00 | 10:00 | 100% | 100% | 100% | 100% | 50% | 30% | 30% | 75%
lodging | 20.0501 | 22.3818 | 16.9437 | 17.62 | 18.2478 | 20.5994 | 18.5747 | lodging | 605.4715 | 679.07 | 682.3879 | 807.5262 | 826.6675 | 707.3686 | 737.794 | lodging | 56000 | 10:00 | 13:00 | 100% | 100% | 100% | 70% | 50% | 100% | 100% | 88.57% | 10:00 | 13:00 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 90%
Manufacturing | 15.5806 | 17.3925 | 13.1667 | 13.6922 | 14.1801 | 16.0075 | 14.4341 | Manufacturing | 499.6061 | 560.336 | 563.0738 | 666.3319 | 682.1265 | 583.6867 | 608.7923 | Manufacturing | 250000 | 13:00 | 15:00 | 100% | 100% | 100% | 70% | 50% | 100% | 100% | 88.57% | 13:00 | 15:00 | 100% | 100% | 100% | 50% | 30% | 100% | 100% | 30%
Special Assembly Auditorium | 170.7753 | 190.6354 | 144.3169 | 150.0774 | 155.4247 | 175.4541 | 158.2091 | Special Assembly Auditorium | 475.887 | 533.7337 | 536.3415 | 634.6974 | 649.7421 | 555.9758 | 579.8895 | Special Assembly Auditorium | 35000 | 15:00 | 18:00 | 100% | 100% | 100% | 50% | 50% | 100% | 80% | 82.86% | 15:00 | 18:00 | 100% | 100% | 100% | 50% | 100% | 100% | 100% | 75%
Default | [7 empty] | Default | [7 empty] | Default | 159673.3333 | 18:00 | 24:00 | 100% | 100% | 100% | 100% | 75% | 100% | 100% | 96.43% | 18:00 | 24:00 | 100% | 100% | 100% | 100% | 50% | 50% | 100% | 50%
(HEAT PUMP with COP = 3 )
Building Type | Heating-HP_Savings_Factor (kWh/1000 SqFt)
| North East (Fort Madison, IA) | North West (Lincoln, NE) | South East (Cape Girardeau, MO) | South West (Kaiser, MO) | St Louis, MO | Kansas City, MO | Average/Unknown (Knob Noster, MO)
Office - Low-rise | 171.339 | 191.2645 | 144.7932 | 150.5727 | 155.9377 | 176.0332 | 158.7312
Office - Mid-rise | 114.3065 | 127.5995 | 96.5968 | 100.4525 | 104.0317 | 117.4381 | 105.8954
Office - High-rise | 153.8188 | 171.7069 | 129.9875 | 135.176 | 139.9924 | 158.033 | 142.5003
Religious Building | 1118.114 | 1248.143 | 944.883 | 982.5988 | 1017.609 | 1148.747 | 1035.8391
Restaurant | 798.8033 | 891.6987 | 675.0436 | 701.9886 | 727.0005 | 820.6882 | 740.0245
Retail - Department Store | 277.4258 | 309.6886 | 234.4438 | 243.8019 | 252.4886 | 285.0265 | 257.0118
Retail - Strip Mall | 183.5981 | 204.9493 | 155.153 | 161.3461 | 167.0949 | 188.6282 | 170.0883
Convenience Store | 134.4212 | 150.0535 | 113.5951 | 118.1294 | 122.3383 | 138.1039 | 124.53
Elementary School | 475.4281 | 530.7172 | 401.7694 | 417.8064 | 432.6929 | 488.4535 | 440.4444
High School | 465.0499 | 519.1321 | 392.9991 | 408.686 | 423.2475 | 477.7909 | 430.8299
College/University | 923.4883 | 1030.8837 | 780.4109 | 811.5617 | 840.4778 | 948.7891 | 855.5347
Healthcare Clinic | 331.0208 | 369.5163 | 279.7353 | 290.9012 | 301.266 | 340.0898 | 306.6631
lodging | 156.7026 | 174.9261 | 132.4244 | 137.7103 | 142.6169 | 160.9958 | 145.1719
Manufacturing | 121.7711 | 135.9322 | 102.9049 | 107.0125 | 110.8253 | 125.1072 | 112.8107
Special Assembly Auditorium | 1334.7038 | 1489.9207 | 1127.9162 | 1172.938 | 1214.7299 | 1371.2706 | 1236.4914
Default
ELECTRIC RESISTANCE
Building Type | Heating-ER_Savings_Factor (kWh/1000 SqFt)
| North East (Fort Madison, IA) | North West (Lincoln, NE) | South East (Cape Girardeau, MO) | South West (Kaiser, MO) | St Louis, MO | Kansas City, MO | Average/Unknown (Knob Noster, MO)
Office - Low-rise | 514.017 | 573.7936 | 434.3796 | 451.7182 | 467.813 | 528.0995 | 476.1937
Office - Mid-rise | 342.9194 | 382.7985 | 289.7904 | 301.3576 | 312.095 | 352.3143 | 317.6861
Office - High-rise | 461.4565 | 515.1208 | 389.9624 | 405.5281 | 419.9771 | 474.0991 | 427.5009
Religious Building | 3354.342 | 3744.4291 | 2834.6489 | 2947.7965 | 3052.8269 | 3446.2409 | 3107.5173
Restaurant | 2396.41 | 2675.0962 | 2025.1307 | 2105.9657 | 2181.0015 | 2462.0645 | 2220.0735
Retail - Department Store | 832.2775 | 929.0657 | 703.3315 | 731.4057 | 757.4657 | 855.0794 | 771.0355
Retail - Strip Mall | 550.7944 | 614.848 | 465.459 | 484.0383 | 501.2846 | 565.8845 | 510.265
Convenience Store | 403.2636 | 450.1604 | 340.7854 | 354.3881 | 367.015 | 414.3118 | 373.59
Elementary School | 1426.2844 | 1592.1516 | 1205.3081 | 1253.4191 | 1298.0786 | 1465.3604 | 1321.3333
High School | 1395.1498 | 1557.3962 | 1178.9972 | 1226.0579 | 1269.7426 | 1433.3727 | 1292.4896
College/University | 2770.4649 | 3092.6511 | 2341.2328 | 2434.6852 | 2521.4334 | 2846.3674 | 2566.6041
Healthcare Clinic | 993.0624 | 1108.5488 | 839.2058 | 872.7035 | 903.798 | 1020.2693 | 919.9892
lodging | 470.1078 | 524.7782 | 397.2733 | 413.1309 | 427.8508 | 482.9874 | 435.5156
Manufacturing | 365.3133 | 407.7967 | 308.7147 | 321.0374 | 332.476 | 375.3217 | 338.4322
Special Assembly Auditorium | 4004.1113 | 4469.7621 | 3383.7485 | 3518.8139 | 3644.1898 | 4113.8119 | 3709.4742
Default
Heating savings -
For gas,
For heat pump,
For electric resistance,
Where, and
Heating savings -
For gas, 〖 𝑄〗_ℎ𝑒𝑎𝑡𝑖𝑛𝑔= (1.08∗ ∆𝑇∗𝐶𝐹𝑀)/(𝜂_𝑏𝑜𝑖𝑙𝑒𝑟∗100,000 𝐵𝑇𝑈/𝑡ℎ𝑒𝑟𝑚)
For heat pump, 𝑄_ℎ𝑒𝑎𝑡𝑖𝑛𝑔= (1.08∗ ∆𝑇∗𝐶𝐹𝑀)/(𝜂_𝐻𝑃∗3,412 𝐵𝑇𝑈/𝑘𝑊)
For electric resistance, 𝑄_ℎ𝑒𝑎𝑡𝑖𝑛𝑔= (1.08∗ ∆𝑇∗𝐶𝐹𝑀)/(3,412 𝐵𝑇𝑈/𝑘𝑊)
Where, 𝜂_𝑏𝑜𝑖𝑙𝑒𝑟=0.8 and 𝜂_𝐻𝑃=3

## HDH65, CDH 65
MO Weather Sites
| HDH65 | CDH65
CAPE GIRARDEAU | 110169.54 | 33823.98
KAISER | 114567.06 | 40026.72
WHITEMAN | 120774.66 | 36570.3
FORT MADISON | 130367.58 | 30011.46
LINCOLN | 145528.44 | 33659.52
ST LOUIS | 118649.1 | 40975.5
KANSAS CITY | 133939.26 | 35062.2
Il Weather Sites
| HDH65 | CDH65
ROCKFORD | 175870.2 | 23524.14
CHICAGO | 155925 | 24335.64
SPRINGFIELD | 135526.68 | 31928.76
BELLEVILLE | 131719.68 | 34495.56
MARION | 113942.16 | 34285.32

## Sheet3
North East (Fort Madison, IA) | North West (Lincoln, NE) | South East (Cape Girardeau, MO) | South West (Kaiser, MO) | St Louis, MO | Kansas City, MO | Average/Unknown (Knob Noster, MO)